## Slide 1
⚡
Transformer Fleet Health
& Replacement Planning
Which transformers to replace or inspect within the budget, and why
Team Rayquaza · HCLTech Future Ready AI Engineer Hackathon · Data Science & ML edition · 11 Oct 2026
Notes: One line: a utility can afford to fix only a few transformers a year. We predict each one's chance of failing in the next 12 months, weigh it by who loses power, and choose replace/inspect actions within the budget, with a reason for each.

## Slide 2
1
The problem
A utility can afford to fix only a few transformers a year
~400 power transformers. A failure can cut power to a hospital or a village and costs far more than a planned replacement.
Oil tests (gases dissolved in the oil) are the best health signal, but many units have never been tested.
Failures are rare, so a model that says "nothing fails" looks accurate and is useless.
User and decision
The asset-planning engineer. With this year's budget: which transformers to replace, which to inspect, which to leave, backed by probabilities they can trust and a reason for every choice.
400
transformers in the fleet
38%
never oil-tested
4.3%
of snapshots fail within 12 months
Notes: Stress the rarity: 138 positive rows out of 3,200 labelled snapshot rows. That shapes every modelling choice: PR-AUC not accuracy, simple models, repeated validation.

## Slide 3
2
Is this a real problem? Yes: industry relevance
Every grid operator faces this decision every year
1
Ageing fleets, fixed budgets
Much of the installed transformer base is decades old, and utilities can replace only a small share each year. Choosing which ones is the core asset-management decision.
2
Failures are expensive and slow to fix
An unplanned failure means emergency replacement, outage penalties and lost supply. New large units can take many months to arrive, so replacements must be planned ahead.
3
Who loses power matters
A hospital, an industrial site and a village feeder are not equal. Planning has to weigh consequence, not just condition.
4
Condition data is sparse
Oil tests (dissolved-gas analysis, the industry-standard health check: IEEE C57.104 / IEC 60599) are sampled, not continuous, and many units have never been tested.
Our formula is the industry's formula
risk = probability of failure
× consequence of failure
Risk-based asset management (ISO 55000) and regulator methods such as the UK's network asset risk methodology rank assets the same way. We add calibrated probabilities, honest uncertainty and a budget optimiser.
Who has this problem
Distribution and transmission utilities, industrial plants, data centres, railways, renewable-energy substations, large campuses and hospitals.
Notes: Keep it qualitative; don't quote numbers you can't source. The point: every utility makes this ranking decision yearly, usually by age or rules of thumb. The PoF x CoF structure matches established risk-based asset management practice (ISO 55000; the UK DNOs' Common Network Asset Indices Methodology uses probability and consequence of failure).

## Slide 4
3
What the system delivers
Every number comes from code; every recommendation has a reason
Failure probability + range
"TR-0102: 19% chance of failing in 12 months (likely 12–28%)". Calibrated, wider when we know less.
Health score per field
100 minus points for gas condition (IEEE C57.104 levels), gas trend, peak load and age. Blank, never "healthy", without an oil test.
Risk ranking
Risk = probability × impact (hospital 5, industry 3, urban 2, rural 1, × customers served), with top factors per unit.
Budget plan
Knapsack picks replace / inspect / nothing within budget, compared with "replace the oldest". Every action needs approval.
Honest about missing data
Untested units: scored_low_confidence, wide range, inspect before any replacement.
New data → new plan
Load a CSV (e.g. inspection results): validate → rebuild → re-score → re-plan → before/after comparison.
Notes: These six map one-to-one to the capabilities table in the HCL guide (section 2.1).

## Slide 5
4
Architecture: the medallion pipeline
Raw → cleaned → business-ready · one command rebuilds everything in ~3 s: python -m src.pipeline
Source
4 CSVs
(Annex B)
►
Bronze
raw, as received
+ _ingested_at
+ _source
►
Silver
cleaned, typed
one row per key
9 checks before write
►
Gold
star schema
4 dimensions
5 facts
►
Model + plan
score, risk
knapsack
►
API + UI
FastAPI
Streamlit
Bronze = the replay tape
Every file kept exactly as received, including what /ingest saved. A bug later is fixed and re-run without the source. Audit trail of what arrived when.
Silver = one place for quality
IDs tidied, duplicates removed, ppb→ppm fixed, gaps left NULL. 9 HCL checks run BEFORE anything is written: bad data stops the run.
Gold = shaped for reading
Star schema with shared dimensions. fact_snapshot is the single, leakage-safe input for the model AND the API: one function builds features for both.
Notes: Say: raw → cleaned → business-ready. Re-runnable: silver and gold are rebuilt in full, two runs give identical tables. Gold written in one transaction (tables created empty first: pandas' CREATE TABLE escapes the transaction).

## Slide 6
5
Star schema: 4 shared dimensions, 5 fact tables
Conformed dimensions: every fact can be sliced the same way
Fact table ↓ / Dimension → | dim_transformer | dim_date | dim_run | dim_action | Grain: one row =
fact_oil_test | ✔ | ✔ |  |  | one transformer × one oil test
fact_operation | ✔ | ✔ |  |  | one transformer × one month
fact_snapshot (model input) | ✔ | ✔ |  |  | one transformer × one quarterly snapshot
fact_risk | ✔ | ✔ | ✔ |  | one scoring run × one transformer
fact_plan | ✔ | ✔ | ✔ | ✔ | one plan × one chosen action
Star, not snowflake
Customer-type weight lives inside dim_transformer: one join fewer, a little repetition accepted.
Surrogate keys
transformer_key is our own stable integer: business IDs arrive messy ("tr-0045 ").
Run history kept
dim_run, fact_risk and fact_plan are never wiped by a rebuild, so before/after new data can be compared.
Notes: Gas, load and temperature are non-additive measures (average or max, never sum). is_failure is additive (sum = number of failures).

## Slide 7
6
Every gold table and how it is used
Built by src/pipeline.py and src/features.py · run history written by the API and the UI
Table | Rows | Key columns / measures | Used for
dim_transformer | 400 | transformer_key, customer_type, customers, region, rating_class, type_weight, impact_weight | risk = p × impact · pricing by size · UI filters
dim_date | 1,188 | date_key (20250101), year, quarter, month, is_snapshot_date | slice any fact by month / quarter
dim_action | 6 | action_key, action (replace/inspect), rating_class, cost | plan prices · fact_plan
dim_run | per run | run_id, created_at, kind, as_of, budget, model_version | compare runs before / after new data
fact_oil_test | 1,016 | 6 gases (ppm), total combustible gas, unit_fixed | gas history · analysis
fact_operation | 14,112 | load %, top-oil temperature, age, is_failure, is_repair | stress history · failure counts
fact_snapshot | 4,800 | 21 features + failed_next_12m (3,200 labelled, 138 positive) | the model's training table
fact_risk | per run | probability, 90% range, health, impact, risk | API /predict · UI re-score
fact_plan | per plan | action, cost, risk before, risk removed | API /plan · UI Approve
Notes: Honest detail if asked: build_features() reads the silver tables, not fact_oil_test / fact_operation, so training and the API compute features identically on fresh data.

## Slide 8
7
The grain, and how we stop the model seeing the future
One row = one transformer at one quarterly snapshot date
History before the date → the INPUTS (21 features)
Snap-
shot
Next 12 months → the ANSWER
SQL window functions
ROW_NUMBER() → the newest usable oil test before the snapshot.
LAG() → the previous test, so we know how fast gases are rising.
A repair resets the pattern: tests count from the month after it.
Labels are NULL, not 0
Quarters after 2025-10-01 don't have 12 months of future in the data yet. Treating "not seen yet" as "did not fail" would quietly corrupt training.
Leakage test, proven
150 random rows recomputed in plain pandas from data before the snapshot only: they match. We planted a leak on purpose (tests 3 months in the future): the test failed. Reverted → passes.
Notes: Why quarterly: oil tests come every 6–12 months, so monthly rows would be near-duplicates and yearly would give too few rows. One shared function, build_features(), is used for training and the API.

## Slide 9
8
How the model is trained
src/model.py · scikit-learn only · seed 42 everywhere
1
Split
Held-out = last 2 labelled quarters × 20% of transformers (160 rows, 9 failures), used ONCE.
2
Candidates
Baselines: age only, health-index rule. Models: LR + median, LR + missing flags, boosting with native NaN.
3
Validate
Grouped by transformer AND time-aware (train on earlier quarters), 5 repeats → mean and range.
4
Choose
Simplest within the noise of the best → logistic regression + median fill.
5
Calibrate
Platt (sigmoid): Brier 0.18 → 0.053. Isotonic rejected: overfits ~40 failures.
6
Range
30 bootstrap copies → 90% range. Untested units get a wider range (0.12 vs 0.07).
7
Explain
Top 3 drivers per unit; permutation importance globally (age leads).
8
Save + serve
models/model.joblib + model card; score() → probability, range, status, health, drivers.
Notes: All filling and scaling sit inside a scikit-learn Pipeline, fitted on training rows only (HCL Annex A). class_weight='balanced' for rare failures; calibration repairs the distorted probabilities. Every configuration logged to reports/experiments.csv.

## Slide 10
9
Results, stated honestly
PR-AUC: are real failures near the top of the list? (guessing = 0.043)
Chart: Grouped, time-aware CV (5 repeats)
| Age only | Health-index rule | LR + median (chosen) | LR + missing flags | Boosting, native NaN
PR-AUC (CV mean) | 0.105 | 0.06 | 0.082 | 0.079 | 0.072
Held-out, used once (9 failures): model 0.104 · age only 0.152 · health rule 0.356. All intervals overlap.
Calibration works
Brier score 0.182 → 0.053 after Platt scaling: a predicted 20% now means about 20%, which the risk formula needs.
Honest verdict
On our synthetic data the model does NOT beat age alone: failures there are driven mostly by age and the gas signal is faint. We keep it because an inspection result must be able to change a unit's risk, and age-only would ignore it. A 4-input version (age + gas/trend/load points) scored 0.117 and beat age-only: our next step.
Notes: HCL: 'a complex model must earn its place'. Say it plainly. The held-out set has only 9 failures, so its numbers are very noisy.

## Slide 11
10
From prediction to decision
Risk = calibrated probability × impact, then a knapsack within the budget
Hospital unit
12,000 customers
impact 5 × 12,000 = 60,000
19% → risk 11,400
Rural unit
2,000 customers
impact 1 × 2,000 = 2,000
25% → risk 500
The hospital unit comes first, even though the rural one is more likely to fail.
Replace removes risk: (p − 1%) × impact
Inspect reveals hidden risk: (p_high − p) × impact: most valuable where we know least
Never replace blind: no recent oil test → inspect only
Knapsack (dynamic programming): ≤ 1 action per unit, cost ≤ budget
Every plan is a proposal: an engineer approves it
Chart: Fleet risk removed at a 5M budget
| Our plan: 7 replacements | Replace oldest: 15 units
Fleet risk removed | 20.9 | 5.6
Plus 226 inspections covering 377,943 of hidden risk, shown separately, never added. Held-out budget test: 10.0% vs 2.3%; acted on 4 real failures vs 2.
Notes: Costs are our assumptions (the panel told us to assume them): replace 150k/350k/700k, inspect 10k/15k/25k by size; budget 5M. Inspection is ~23x cheaper, so a fixed % value would inspect everything; tying it to uncertainty sends inspections where they tell us something.

## Slide 12
11
Mentor feedback, and what we built
"If an inspection shows it is worse than predicted, its risk should go up."
Inspection
►
= new oil test
►
/ingest or UI
►
Validate +
rebuild
►
Re-score
►
Re-plan
Live in the UI: the rehearsal file re-scores 40 transformers. A worse unit's risk rises, its range narrows, and the next plan replaces it.
Panel said (12:00 review) | What we did
Inspection results should raise risk | Inspection = new oil test → loader → rebuild → re-score → re-plan; before/after table in the UI
Assume replacement / inspection costs and the budget | replace 150k / 350k / 700k · inspect 10k / 15k / 25k · budget 5M (late drop 4M)
Which libraries for data, models, everything? | pandas/numpy · SQLite/SQLAlchemy · scikit-learn/joblib · FastAPI · Streamlit · pytest
Docker is optional | Removed; requirements.txt pinned to the exact versions we tested with
Notes: This slide answers 'did you act on feedback?'. Demo it live on UI screen 4.

## Slide 13
12
Every edge case, handled on purpose
All six HCL traps were planted in our data, so each one can be shown
Edge case | How we handle it | Where
No oil test at all (38%) | has_oil_test feature · low confidence · wider range · health blank, never "healthy" · inspect first | features · model · plan
Old units with few tests | low confidence (one test) · wide range | model
Look-alike pair: hospital vs rural | same probability, very different impact → the hospital ranks far higher | dim_transformer · plan
Gas jump from a unit change (ppb) | a test ≥ 200× the unit's other tests → ÷1000 and flagged (found exactly the 3 planted) | silver
Recent repair resets the pattern | gas features use only tests from the month after the latest repair / failure | features
Budget can't cover all high-risk units | knapsack takes the best risk per unit of money; the rest wait | plan
Duplicates, messy IDs, gaps | strip().upper() · one row per key, last loaded wins · gaps stay NULL | silver
Judges' files without our extra columns | no rating_class → medium (flagged) · no event → none | silver
Renamed column · bad rows in uploads | COLUMN_ALIASES config · rows rejected with a reason · rollback if validation fails | loader
Notes: Validation output: reports/validation_output.txt: 5 duplicate assets removed, 6 duplicate rows, 3 ppb tests converted, 282 gaps left NULL, 9/9 checks pass.

## Slide 14
13
The interface: the engineer's workflow
streamlit run ui/app.py · calls the same functions as the API
1
Fleet risk ranking
Where is the risk? KPIs, ranked table, filters, low-confidence badges.
2
Transformer detail
Why? Probability + range, health points per field, gas history with ppb fix and repairs.
3
Budget plan
What do we do? Our plan vs replace-oldest, removed vs revealed risk, Approve.
4
New data & what changed
Upload inspection results → re-score → before/after → plan changes.
5
Model & data quality
Reliability chart: does a predicted 20% mean ~20%? Plus the 9/9 validation report.
Where is the risk → why → what do we do → what changed → can we trust it
Notes: Demo order: 1 → 2 (a tested unit, then an untested one) → 3 (5M, then 4M) → 4 (rehearsal file) → 5. Reset on screen 4 before presenting.

## Slide 15
14
How we validated, including the AI's work
AI assistants wrote most of the code; we specified the design and checked everything
9/9
HCL validation checks
101
automated tests pass
36/36
independent data-spec checks
What we checked
Leakage test proven by planting a leak · row counts at every join (validate="many_to_one") · two runs give identical tables · every UI screen run headless against the real model · every reported number read for plausibility.
Mistakes we caught
1. Plan claimed "108.9% of risk removed": revealed risk was added to removed risk. Now reported separately.
2. A test passed for the wrong reason (missing column, not the future date). Fixed the test.
3. Scoring as of 2026-10-01 would have ignored the late-drop oil tests (dated Oct 1–10).
4. requirements pinned pandas 2.2.3; the code was tested on 3.0.0. Re-pinned.
5. A push added a nested repo pointer instead of the data. Removed.
Notes: Every commit was made by a team member by hand. The written team contract (docs/team/SHARED_CONTRACT.md) is what every AI session followed.

## Slide 16
15
Libraries, by job
Small, standard stack: nothing to break on venue wifi
Job | Library | Used for
Data generation | numpy, pandas | seeded synthetic fleet with planted edge cases, data card
Storage + pipeline | SQLite, SQLAlchemy, pandas | bronze / silver / gold, transactions, window-function SQL
Model | scikit-learn, joblib | logistic regression, boosting, imputation, pipelines, grouped CV, calibration, metrics
Budget optimiser | plain Python (dynamic programming) | knapsack: explainable line by line, no solver needed
Serving | FastAPI, Uvicorn, Pydantic v2, python-multipart | /predict /plan /ingest /model/info /explain /health
Interface + charts | Streamlit, matplotlib | 5 screens, gas history, reliability chart
Testing | pytest, httpx | 101 tests, including leakage and API contract
Notes: Docker was in the HCL stack; the panel confirmed it is optional, so we removed it and pinned exact versions instead.

## Slide 17
16
How it scales
The grain and the shared feature function stay; only the engine underneath changes
Area | Today | At scale
Storage | SQLite, one file | PostgreSQL; bronze as Parquet partitioned by month; indexes on (transformer_id, test_date) and (transformer_id, month)
Loading | full rebuild, ~3 s | incremental: watermark on _ingested_at, upsert into silver, only the new quarter's snapshots
History | SCD Type 1 (overwrite) | SCD Type 2 on dim_transformer: keep customer / size changes over time
Model | retrained by hand | scheduled monthly retraining, drift + calibration monitoring; versions already in dim_run
Optimiser | DP: 400 units × 1,000 budget steps | integer programming (OR-Tools / PuLP) or greedy by value-per-cost for 10k+ units
API | one Uvicorn process | stateless → several workers behind Nginx; nightly precomputed fact_risk
UI | scores live | reads precomputed fact_risk; live scoring only for what-if questions
Deployment | our laptops | containers on a Linux server
Notes: Features are set-based SQL with window functions: cost grows linearly with transformers × quarters, and the same SQL runs inside Postgres.

## Slide 18
17
From prototype to product: taking it to market
Start with one utility, prove it on their own history, then grow by assets and by customers
1
Pilot
One utility region. Load their history, back-test: would our plan have caught last year's failures better than their current method?
►
2
Integrate
Connect real sources: lab oil-test results, meter / SCADA loading, GIS map of who each transformer feeds, work-order history.
►
3
Expand assets
Same pattern (grain + features + probability × consequence + budget optimiser) for breakers, cables, poles, substations.
►
4
Platform
Many utilities on one product: benchmarking across fleets, live sensor feeds, a model per utility, approvals built in.
Who pays, and how
Utilities and large asset owners. Subscription priced per asset monitored; deployed in their environment because grid data is sensitive.
The value we sell
More risk removed for the same budget (in our test: 20.9% vs 5.6% for replacing the oldest), fewer unplanned outages, and a defensible, auditable plan.
Why it can scale
Schema mapping is configuration, not code; one feature function for training and serving; every plan approved by an engineer, which builds trust.
Notes: This is the business path, not the technical one (previous slide). Key message: the pilot proves value on the customer's OWN past failures before anything is sold; the same architecture then repeats per asset class and per utility.

## Slide 19
18
With more time, we would…
Ordered by impact
1
Ship the 4-input model
Age + gas/trend/load points beat age-only in CV (0.117 vs 0.105). Re-run the held-out test once.
2
Real failure history
Synthetic data mostly encodes age. Real outage records would give the gas signal its true weight.
3
Time-to-failure
A survival model for "how many months left", not just "fails within 12 months".
4
Inspection outcomes
Learn what inspections actually find, so the value of an inspection is measured, not assumed.
5
Incremental + Postgres
Watermarked loads, SCD Type 2 history, nightly scoring: the scaling path on the previous slide.
6
Monitoring
Drift on inputs, calibration over time, alerts when the model goes stale; retraining plan.
7
UI through the API
One serving path, authentication and roles (engineer approves, planner proposes).
8
Cost of a miss
Use real outage costs per customer type instead of fixed weights; test sensitivity of the plan.
Notes: Lead with 1 and 2: they answer the honest model result.

## Slide 20
19
Trade-offs: what we chose, what we rejected
Criterion: the simplest design that works, and why
Decision | Chose | Rejected | Why
Pipeline | medallion | one script raw → model | replayable, auditable; quality enforced once
Gold layer | star, conformed dimensions | 3NF / snowflake | read-heavy: fewer joins win
Grain | quarterly snapshots | monthly / yearly | tests every 6–12 months: monthly = duplicates, yearly = too few
Refresh | full rebuild (~3 s) | incremental | at this size incremental only adds failure modes
Model | logistic regression | boosting by default | few failures; readable weights; boosting didn't win
Calibration | Platt (sigmoid) | isotonic | isotonic overfits ~40 failures
Inspection value | uncertainty-based | fixed % of risk | inspection ~23× cheaper: a fixed % inspects everything
UI | same functions as API | UI → HTTP → API | one copy of the logic
Packaging | local run | Docker | panel confirmed optional
Notes: If asked about any row: state what we chose, what we rejected, and the one-line reason.

## Slide 21
Thank you: questions?
Leakage-safe by design · honest about uncertainty · every decision explained and approved by a person
pip install -r requirements.txt
python -m src.pipeline # bronze → silver → gold
python -m src.model # train + evaluate
uvicorn src.api:app # API :8000/docs
streamlit run ui/app.py # UI :8501
Unique0202: architecture, pipeline, features, loader, UI, README
sreerajmahesh: synthetic data, FastAPI service
abinavhub: models, validation, calibration, plan
Notes: Close on the three ideas: leakage-safe grain, honest uncertainty, human approval.